# Text boxes

Main Shut off Valve

PRV #1 – Set at 125 psi - Install BEFORE Fire Sprinkler / Domestic Water Split

Check Valve

Flow Switch

Domestic Water

Domestic Shut off Valve

PRV #2

Fire Sprinkler System

Pressure Gauge – Shows the City Pressure

Pressure Gauge – Shows the Reduced Pressure

Pressure Gauge – Shows  the pressure in Fire Sprinkler System

Pressure Relief Valve SET AT

175 psi

This PRV serves a fire sprinkler system and shall be set at 125psi.

SIGN

Inspector Test / Drain Valve